## Below 200k
REG_ID | Reg ID Description | Time | Areas | Planning methodology | Proposed time in 2024 DTAPR | Reason for change
DOC_11.03.38 | Optical Arc Fault Protection | 2026,2027,2028,2029,2030, | Homebush,OATLEY,Sydney CBD,Sydney Northwest | The optical arc fault protection program is driven by the need to protect the safety of workers so far as is reasonably practicable at substations. The present summated current protection schemes are inadequate and will be replaced with the modern standard optical arc fault protection systems. The modern optical arc fault protection systems will also operate to limit the damage to other network assets. | 2025,2026,2027,2028,2029, | No Change
DOC_11.03.54 | Asbestos Fire Doors - ZN & TS | 2028 | Sydney CBD | The primary function of a fire door is to prevent the spread of fire. Asbestos contained within these fire doors is a safety risk to workers and the public. Ausgrid has a duty of care to eliminate or where this is not practicable minimise safety risks to as low as is reasonably practicable. | 2026,2027,2028,2029, | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Overhead Mains Reconfiguration - Streetli | 2026,2027,2028,2029 | Homebush,Lower Hunter ,Newcastle ,OATLEY,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025,2026,2027,2028,2029, | No Change
REP_01.02.52 | RMU & Fuse Switch Replacement | 2026,2027,2028,2029,2030, | Homebush,Lower Hunter ,Newcastle ,OATLEY,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest | This program funds the replacement of 11kV Ring Main Isolators (RMIs) & Fuse Switches (FS) that have been approach their end of life. Projects within this program are identified based on an asset condition risk assessment.. | 2025,2026,2027,2028,2029, | No Change
REP_01.02.59 | SCADA Equipment - DC | 2027,2028,2029,2030 | Sydney CBD | The SCADA equipment in Sydney CBD distribution centres were installed in early 1990s is now approaching end of life and is increasingly difficult to maintain. | 2026,2027,2028,2029, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Circuit Breaker Replacement - LV | 2026,2027,2028,2029,2030, | Sydney CBD | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025, 2026, 2027, 2028, 2029 | No Change
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 2026,2027,2028,2029,2030, | Sydney CBD | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025, 2026, 2027, 2028, 2029 | No Change
REP_01.03.13 | Bass & Saunders Isolation & Earthing Switc | 2026,2027,2028,2029,2030, | Sydney CBD | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2025, 2026, 2027, 2028, 2029 | No Change
REP_02.02.62 | SCADA Equipment - ZN & TS | 2026,2027,2028,2029,2030, | Newcastle ,OATLEY,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest,Upper Hunter , | The SCADA equipment in Sydney CBD zone substations have conditional and aging issues. Considering the high reliability requirement in the CBD area, they are recommended to be replaced. | 2025,2026,2027,2028,2029, | No Change
REP_02.03.05 | Bushing Replacement - ZN & TS | 2027,2028,2029,2030 | Homebush,Ourimbah,Sydney CBD,Sydney Northwest,Upper Hunter | Oil Impregnated Paper transformer bushings poses risk of explosive failure, which represent a safety hazard and can cause excessive damage to substation equipment. Following the catastrophic failure of several oil impregnated paper bushings on Ausgrid’s network, investigations were carried out into the condition of these assets. The investigations found that there was a degradation of the insulation material resulting in water ingress in the bushing. The seriousness of bushing failures instigated a proactive replacement program of this type of oil impregnated paper bushings. The bushing replacement programs form part of Ausgrid’s strategy to meet its obligations to manage the risks of these assets failing so far as is reasonably practicable. | 2025,2026, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.03.07 | Protection Relays - ZN & TS | 2026,2027,2028,2029 | Homebush,Newcastle ,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest | This program is to replace the protection relays that are in poor condition. Failure of protection relays put primary assets at risk and can lead to safety incidnts, property damage and loss of supply. Projects are identified using a condition assessment process. | 2025,2026,2027, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.03.11 | Batteries and Battery Charging Equip - ZN | 2026,2027,2028,2029,2030, | Homebush,Newcastle ,Sydney CBD,Upper Hunter | Failure of the battery scheme whilst the substation is energised can result in the loss of power to the substation’s electrical protection systems. The dominant failure mode of batteries is the loss of capacity due to an internal fault of the cell, which is a nonrepairable failure mode and requires replacement to ensure the battery meets substation performance requirements. ..Batteries that have degraded are unable to hold charge and will not operate when required. The degradation of battery systems means that they need to be replaced to provide the required function. Battery chargers are matched to the battery technology and therefore need to be replaced upon battery technology change to maintain compatibility | 2026,2027,2028,2029, | No Change
REP_04.02.01 | Overhead Mains Replacement - HV (km) | 2026,2027,2028,2029,2030, | Homebush,Lower Hunter ,Newcastle ,OATLEY,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest | Protective galvanised coating of the steel mains and conductor ties degrades with age and can pose environmental risks, such as fires, public safety and failure of supply. Replacement of the steel mains are identified using an condition assessment process that used inspection, spatial risk factors and failure data. | 2025,2026,2027,2028,2029, | No Change
REP_04.02.05 | Underground Cable Replacement - LV (km) | 2026,2027 | Homebush,Lower Hunter ,OATLEY,Sydney CBD,Sydney Northeast,Sydney Northwest | Ausgrid has approximately 785km of Low Voltage underground metallic sheathed cable which supply electricity from distribution substations to customers. LV metallic sheathed cable failures can result in consequences including safety risks, fire risk, unserved energy and other risks. A planned replacement strategy has been adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment. | 2025,2026,2027,2028,2029, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.11 | UGOH Replacement - HV | 2026,2027,2028,2029,2030, | Lower Hunter ,Newcastle ,OATLEY,Ourimbah,Sydney Northeast, | Unlike modern UGOHs which use heat shrink insulation, pot head UGOHs can fail explosively as the cables are terminated inside an oil/compound filled metal casing. The failure of pot head UGOHs is exacerbated by being located in outdoor public areas. Potential hazards include injury to public and staff, live conductors falling to the ground. | 2025,2026,2027,2028,2029, | No Change
REP_04.02.12 | LV Metallic Sheathed Cables | 2026,2027,2028,2029 | Sydney CBD | Low voltage metallic sheathed cable failures can result in consequences such as safety risks, fire risks, unserved energy and other risks. A planned replacement strategy is adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment of Ausgrid's metallic sheathed cable population. | 2025,2026, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.32 | Switch Overhead Replacement - HV | 2026,2027,2028,2029 | OATLEY,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest | Air break switches are installed at the top of poles located in public areas. Ausgrid workers stand directly below the air break switches when network switching is undertaken. The need to replace these air break switches has been triggered by a combination of condition and design related issues which have resulted in safety risks to the public, customers and workers due to uncontrolled discharge of electricity or falling components, as well as network reliability risks associated with these failures. Ausgrid workers have experienced ‘near miss’ safety incidents due to failed porcelain insulators falling during network switching and have received electric shocks from poles due to the uncontrolled discharge of electricity from cracked insulators. A functionally failed air break switch is one that has degraded to the point that it is no longer able to be safely operated or has caused a network interruption due to component failure.
REP_04.04.01 | Overhead Mains Replacement - LV (km) | 2026,2027,2028,2029,2030, | Homebush,Lower Hunter ,Newcastle ,OATLEY,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest | Degradation of overhead conductors and conductor ties can result in fallen conductors which pose risks to public safety and loss of network supply. This program funds the replacement of conditionally failed LV overhead conductor. It is to replace the overhead conductor including the replacements of all conductor phases in any conductor bay or strain section. The scope also includes sections of dedicated LV circuits of bare or PVC insulated construction that must be replaced when dthey are not able to be removed through transferral to LV mains. | 2025,2026,2027, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.04.02 | Underground Cable Replacement - HV (km) | 2030 | Sydney CBD | 11kv and 5kV underground cables experience failures primarily due to age related degradation, moisture ingress or mechanical damage. The risks of failures may include network fires, public safety and loss of supply. This program funds the replacement of conditionally failure HV underground cables and the replacement of structurally/conditionally failure sections of the pit and duct system within the Sydney CBD. The scope is 'like for like' replacement.
REP_04.04.11 | Pillar & Pillar Equipment Replacement | 2030 | Homebush,Lower Hunter ,OATLEY,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest,Upper Hunter | Distribution equipment degradation can be influenced by tdheir age, deisng/material and operating environment. Failures of equipment can pose risks such as network fires, public safety and loss of supply. The risk is primarily managed through established maintenance process and replacement of the equipment.

## Above 200k
REG_ID | Reg ID Description | Notif # | Notif Desc | Year of Work | Area of work | Planning methodology | Proposed time in 2024 DTAPR | Reason for change
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700204106 | REP 137m CONSAC S002199_2 WILLIAM ST SE | 2026 | WOOLLOOMOOLOO | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700201718 | REP 183m CONSAC S002228_1 MAROUBRA SEALS | 2026 | MAROUBRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700200743 | REP 186m CONSAC S002690_3 BOTANY RD EAST | 2026 | BANKSMEADOW | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700203781 | REP 127m CONSAC S004047_2 VICTORIA AV E | 2026 | CHATSWOOD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700202765 | REP 475m CONSAC S005346_2 FRANCIS GREENW | 2026 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235498 | REP HVCB_S15 S001514 Smith Chap | 2026 | SUMMER HILL | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700205046 | REP 310m CONSAC S009920_4 WRIGHT CL.U.G | 2026 | HEATHCOTE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222057 | REP SCB S001224 MILLER IBIS HOUSE | 2026 | NORTH SYDNEY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700201783 | REP 134m CONSAC S005857_3 KING ST STH | 2026 | ERSKINEVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700202761 | REP 142m CONSAC S004004_2 BOTANY RD EAST | 2026 | MASCOT | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700200781 | REP 171m CONSAC S003167_4 CAMERON ST OH | 2026 | EDGECLIFF | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700241731 | REP 125m HDPE S002340_2 PUNCHBOWL RD EAS | 2026 | LAKEMBA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700176321 | REP SCB Sub - S003479 CLARKE COMMERCIAL | 2026 | CROWS NEST | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700839440 | Replace Defective Kiosk S15668 (Project) | 2026 | AVALON BEACH | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700205324 | REP 158m CONSAC S000602_6 FORBES ST UG | 2026 | WOOLLOOMOOLOO | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700204922 | REP 138m CONSAC S000135_5 STAFFORD ST UG | 2026 | DOUBLE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700200702 | REP 626m CONSAC S005447_2 PARKHILL CRES | 2026 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700203663 | REP 160m CONSAC S002139_4 NORTH TERRACE | 2026 | BANKSTOWN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700201973 | REP 146m CONSAC S002302_7 5_15 FARRELL A | 2026 | DARLINGHURST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700202033 | REP 218m CONSAC S002899_3 WALKER ST E U | 2026 | NORTH SYDNEY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700200958 | REP 512m CONSAC S005447_1 PARKHILL CRES | 2026 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2029 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700204598 | REP 174m CONSAC S010011_1 CALVARY HOSPI | 2026 | BEVERLEY PARK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235320 | REP HVCB_P4 S000592 Dunbar St | 2026 | WATSONS BAY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700200891 | REP 187m CONSAC S004530_1 BOTANY RD UG | 2026 | BOTANY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700240929 | REP 124m HDPE S002455_2 BUNNERONG RD | 2026 | EASTGARDENS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700203593 | REP 193m CONSAC S008907_5 MOORE ST UG | 2026 | BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700201697 | REP 208m CONSAC S006841_1 OBSERVATORY HI | 2026 | MILLERS POINT | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700200919 | REP 125m CONSAC S004248_3 LIVERPOOL ST E | 2026 | DARLINGHURST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2029 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700201993 | REP 447m CONSAC S000602_3 HARMER ST UG | 2026 | WOOLLOOMOOLOO | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700204706 | REP 265m CONSAC S010253_1 QUEEN VICTORI | 2026 | BEXLEY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700203944 | REP 172m CONSAC S000135_3 WILLIAM NEW | 2026 | DOUBLE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700204908 | REP 177m CONSAC S002960_1 KIPPAX ST W OH | 2026 | SURRY HILLS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235496 | REP HVCB_LMT S001218 Marple Colgate No 1 | 2026 | VILLAWOOD | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700202208 | REP 747m CONSAC S002143_1 O SULLIVAN RD | 2026 | ROSE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700203195 | REP 125m CONSAC S004047_3 VICTORIA AV W | 2026 | CHATSWOOD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700203253 | REP 157m CONSAC S000096_5 KINTORE ST | 2026 | DULWICH HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700205396 | REP 164m CONSAC PT00916_2 RALEIGH ROAD N | 2026 | MILPERRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700201451 | REP 262m CONSAC S003692_7 CRAIGEND ST E | 2026 | DARLINGHURST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700204792 | REP 168m CONSAC S008907_4 HENDERSON ST & | 2026 | BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700240670 | REP 153m HDPE S004567_5 GLENVIEW ST | 2026 | DARLINGHURST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700205163 | REP 125m CONSAC S000104_5 NICHOLSON ST N | 2026 | WOOLLOOMOOLOO | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700204730 | REP 166m CONSAC S004034_2 WARRANE ROAD N | 2026 | NORTH WILLOUGHBY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700201695 | REP 213m CONSAC S005577_2 GILCREST PL U | 2026 | BALMAIN EAST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700200681 | REP 640m CONSAC S035893_2 CRANBROOK ROAD | 2026 | ROSE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700204660 | REP 152m CONSAC S003692_1 CRAIGEND ST & | 2026 | DARLINGHURST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700848689 | REP OBKS D.S.S015638 Farview Monterey | 2026 | BILGOLA PLATEAU | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700245555 | REP 151m HDPE S001030_1 MATRAVILLE RSL | 2026 | MATRAVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700205431 | REP 194m CONSAC PT10895_1 FOREST RD STH | 2026 | LUGARNO | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700200936 | REP 148m CONSAC S005472_2 MALABAR RD NOR | 2026 | SOUTH COOGEE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2029 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700201696 | REP 265m CONSAC S005577_3 HART ST UG & | 2026 | BALMAIN EAST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700204369 | REP 129m CONSAC S000020_1 MITCHELL RD NT | 2026 | ALEXANDRIA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700201676 | REP 431m CONSAC S038810_3 BERESFORD RD S | 2026 | ROSE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700205329 | REP 120m CONSAC S008637_4 BOTANY RD E/S | 2026 | MASCOT | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700203014 | REP 234m CONSAC S008907_6 HENDERSON ST & | 2026 | BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235375 | REP HVCB_P4 S005080 Muriel Northgate | 2026 | HORNSBY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700203246 | REP 246m CONSAC S008907_1 HENDERSON ST & | 2026 | BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700203650 | REP 465m CONSAC S009839_3 NULLABOR PL U | 2026 | YARRAWARRAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700203929 | REP 323m CONSAC S000104_2 NICHOLSON ST N | 2026 | WOOLLOOMOOLOO | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
DOC_11.03.73 | Overhead Mains Reconfiguration - Streetli | 1700354312 | DOC LV RECONFIG SLCP1388 POLE PY72788 | 2026 | LINDFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.78 | Decommission CBD Vault | 1700208992 | DECOM S000840 PITT ST STRAND | 2026 | SYDNEY | Several underground or vault distribution substations located in the Sydney CBD network area are no longer required, with no plans to rebuild a distribution substation on site for the foreseeable future. To prevent these sites from becoming a safety hazard for Ausgrid’s personnel and the public, there is an obligation to disconnect cables, dismantle equipment and remediate the sites. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700168108 | REP BK S001392 Medicentre St Leonards | 2026 | ST LEONARDS | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700168110 | REP BK S001745 Warringah Rd. | 2026 | MOSMAN | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700168116 | REP BK S001921 St Johns Rd | 2026 | AUBURN | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700168182 | REP BK S001705 Royal St. | 2026 | MAROUBRA | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700168201 | REP BK S000490 Temple St | 2026 | STANMORE | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700283053 | REP MUSK HS72234 IRON BARK AVEUNE | 2026 | MUSWELLBROOK | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700283055 | REP MUSK HS72186 WOOLLYBUTT WAY | 2026 | MUSWELLBROOK | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700283098 | REP MUSK HS72454 SHOPPING PLAZA | 2026 | MUSWELLBROOK | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700291993 | REP MK S015979 WAR VETERANS KITCHEN | 2026 | NARRABEEN | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700292005 | REP MK S016078 ROBERTSON ST 10 | 2026 | NARRABEEN | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700839460 | REP MK S015474 Fisher Rd | 2026 | DEE WHY | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700848674 | REP OBKS D.S.S010719 Banks Cecil | 2026 | MONTEREY | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700848677 | REP OBKS D.S.S010349 Moate Gordon | 2026 | BRIGHTON-LE-SANDS | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.42 | Outdoor Enclosure Substations | 1700376745 | REP OIL RMU S004283 TALAVERA KHARTOUM - | 2026 | MACQUARIE PARK | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396315 | REP OE S002464 MISSOURI PLACE | 2026 | RIVERWOOD | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396317 | REP OE S004729 MADDOX BOURKE | 2026 | ALEXANDRIA | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396320 | REP OE S005993 SIR JOSEPH MYRTLE - PD | 2026 | BANKSTOWN | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396335 | REP OE S001306 LAYTON ST | 2026 | CAMPERDOWN | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396339 | REP OE S009333 TAREN BOX NO 1 | 2026 | TAREN POINT | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396343 | REP OE S001269 MILPERRA VIC | 2026 | REVESBY | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396408 | REP OE S006315 POWER LOVERIDGE | 2026 | ALEXANDRIA | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700808824 | REP OE S003866 Lymoore Sefton | 2026 | THORNLEIGH | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700176287 | REP SCB Sub - S000297 RAINBOW MOUNT | 2026 | COOGEE | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222050 | REP SCB S001963 COPE WELL | 2026 | WATERLOO | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222072 | REP SCB SUB S004248 PMG DARLINGHURST | 2026 | DARLINGHURST | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222084 | REP SCB SUB S003382 WEST CHURCH | 2026 | NORTH SYDNEY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235307 | REP HVCB_P4 S005051 Telecom North Sydney | 2026 | NORTH SYDNEY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235364 | REP HVCB_J18 S002533 Goldman Lane* | 2026 | DOUBLE BAY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235409 | REP HVCB_LMT HS22447 Charlestown Square | 2026 | CHARLESTOWN | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235412 | REP HVCB_P4 S006432 Grosvenor Grafton | 2026 | BONDI JUNCTION | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235413 | REP HVCB_P4 S000819 Luff St | 2026 | BOTANY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235418 | REP HVCB_P4 S005382 Ctal Friendship Rd | 2026 | PORT BOTANY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235436 | REP HVCB_L S001003 Caledonian Rd | 2026 | ROSE BAY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235439 | REP HVCB_J18 S002302 Darlinghurst Vic | 2026 | DARLINGHURST | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235452 | REP HVCB_LMT S016194 Manly Hospital No 1 | 2026 | MANLY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235458 | REP HVCB_LMT S002582 Anzac Wal | 2026 | KINGSFORD | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235464 | REP HVCB_P4 S001685 Canterbury Park | 2026 | CANTERBURY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235467 | REP HVCB_F100 S006229 Holden Liverpool | 2026 | ASHFIELD | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235472 | REP HVCB_S15 S004417 Ryde School Of Food | 2026 | WEST RYDE | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235531 | REP HVCB_S15 S001293 American Flange | 2026 | VILLAWOOD | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235532 | REP HVCB_S15 S003455 Carlingford Shopp N | 2026 | CARLINGFORD | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235544 | REP HVCB_S15 S002819 De Havilland Bankst | 2026 | BANKSTOWN | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235545 | REP HVCB_S15 S003297 Marigold Betts No 1 | 2026 | REVESBY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235588 | REP HVCB_S15 S003535 Csiro Bradfield | 2026 | LINDFIELD | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700237941 | REP HVCB_F100 S001440 Carshalton St. | 2026 | CROYDON PARK | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.61 | Intertripping Schemes - DC | 1700438708 | REP 11KV IT PROT S003237 PENNYS LANE | 2026 | POTTS POINT | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438716 | REP 11KV IT PROT S003646 WEMYSS WENT | 2026 | SURRY HILLS | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438721 | REP 11KV IT PROT S003692 NIMROD ST | 2026 | DARLINGHURST | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438529 | REP SCADA SYSTEM TS00402 ERARING STS | 2026 | ERARING | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438532 | REP SCADA SYSTEM ZN07481 DARLING HARBOUR | 2026 | PYRMONT | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438612 | REP SCADA SYSTEM TS07170 SURRY HILLS STS | 2026 | SURRY HILLS | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438619 | REP SCADA SCHEME TW07310 MASON PARK STSS | 2026 | HOMEBUSH | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374870 | REP NER R1 TS00402 ERARING | 2026 | ERARING | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700756324 | REP NER R2 TS00402 ERARING | 2026 | ERARING | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700214277 | REP 491m CONSAC HS52120_1 FERN PLACE | 2026 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700214278 | REP 478m CONSAC HS52120_2 FERN PLACE | 2026 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700214279 | REP 217m CONSAC HS52120_3 FERN PLACE | 2026 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700214280 | REP 134m CONSAC HS52120_4 FERN PLACE | 2026 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700721010 | REP 173m HDPE S000183_6 ROSCOE ST N/W UG | 2026 | BONDI BEACH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
DOC_11.03.78 | Decommission CBD Vault | 1700735415 | DECOM S000431 Elizabeth St St James | 2027 | SYDNEY | Several underground or vault distribution substations located in the Sydney CBD network area are no longer required, with no plans to rebuild a distribution substation on site for the foreseeable future. To prevent these sites from becoming a safety hazard for Ausgrid’s personnel and the public, there is an obligation to disconnect cables, dismantle equipment and remediate the sites. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.78 | Decommission CBD Vault | 1700735417 | DECOM S000428 Bridge & George | 2027 | SYDNEY | Several underground or vault distribution substations located in the Sydney CBD network area are no longer required, with no plans to rebuild a distribution substation on site for the foreseeable future. To prevent these sites from becoming a safety hazard for Ausgrid’s personnel and the public, there is an obligation to disconnect cables, dismantle equipment and remediate the sites. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321614 | REP W TYPE KIOSK S010370 QUEENS BAY | 2027 | BRIGHTON-LE-SANDS | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321617 | REP T TYPE KIOSK S010443 BESTIC FISHERME | 2027 | KYEEMAGH | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321619 | REP S TYPE KIOSK S010469 FOREST KINSEL | 2027 | BEXLEY | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321620 | REP T TYPE KIOSK S010021 LETITIA WONOONA | 2027 | OATLEY | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321622 | REP S TYPE KIOSK S010477 ALLWOOD GULL | 2027 | LUGARNO | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321623 | REP S TYPE KIOSK S010478 SUNSHINE WATERS | 2027 | PEAKHURST HEIGHTS | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321624 | REP S TYPE KIOSK S010480 CAMBRIDGE PERCI | 2027 | PENSHURST | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700291635 | REP MK S016156 WESTERN AV | 2027 | NORTH MANLY | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321637 | REP S TYPE KIOSK S010520 VILLIERS RAILWA | 2028 | ROCKDALE | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700291636 | REP MK S016103 TOTALA PL | 2028 | ELANORA HEIGHTS | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321642 | REP W TYPE KIOSK S010526 PRESIDENT LACHA | 2028 | KOGARAH | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321643 | REP W TYPE KIOSK S010528 GLOUCESTER FORE | 2028 | HURSTVILLE | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700291638 | REP MK S016135 MATHEWS ST | 2028 | DAVIDSON | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700291639 | REP MK S015962 UNDULA PL | 2028 | BELROSE | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321645 | REP W TYPE KIOSK S010532 CHUTER PARK | 2029 | SANS SOUCI | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700291640 | REP MK S016010 KYEEMA PDE | 2029 | BELROSE | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321646 | REP W TYPE KIOSK S010533 OATLEY NEVILLE | 2029 | OATLEY | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700291641 | REP MK S016057 ANNAM ROAD N | 2029 | BAYVIEW | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700291642 | REP MK S016166 NARRAWEENA PUB SCHOOL | 2029 | NARRAWEENA | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321648 | REP W TYPE KIOSK S010534 QUEEN FIRTH | 2029 | ARNCLIFFE | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321649 | REP W TYPE KIOSK S010535 VICTORIA CROSS | 2029 | MORTDALE | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321650 | REP W TYPE KIOSK S010537 CLAREVILLE MINT | 2030 | SANS SOUCI | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321651 | REP W TYPE KIOSK S010538 ALFRED FLORENCE | 2030 | RAMSGATE BEACH | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700291643 | REP MK S015247 BROOKER AVENUE | 2030 | BEACON HILL | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321652 | REP W TYPE KIOSK S010541 BATH CHUTER | 2030 | MONTEREY | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700291644 | REP MK S015996 BURCHMORE RD | 2030 | MANLY VALE | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321653 | REP W TYPE KIOSK S010544 RUTLAND LANCELO | 2030 | ALLAWAH | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.02 | Distribution Subs - Kiosk Replacement | 1700321654 | REP W TYPE KIOSK S010545 MCMILLAN CLAREV | 2030 | SANDRINGHAM | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396316 | REP OE S004431 TALAVERA EDEN PARK | 2027 | MACQUARIE PARK | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396321 | REP OE S000055 UNDERWOOD RD | 2027 | HOMEBUSH | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396324 | REP OE S010904 WEST BOTANY DMR | 2027 | ROCKDALE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396328 | REP OE S001254 METAL COATINGS | 2027 | GREENACRE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396330 | REP OE S001363 MADELINE HOPE NO 2 | 2027 | ENFIELD | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396332 | REP OE S001275 BIRMINGHAM AV NTH NO 1 | 2027 | VILLAWOOD | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396333 | REP OE S001471 HILLEMMA | 2027 | LEICHHARDT | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396336 | REP OE S001209 BANKSTOWN TIMBER | 2027 | BANKSTOWN | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396338 | REP OE S001724 DURHAM MEMORIAL | 2027 | ST IVES | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396340 | REP OE S000608 BONDS SKINNER | 2027 | PUNCHBOWL | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396344 | REP OE S001797 SHEFFIELD ST | 2027 | KINGSGROVE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396346 | REP OE S010269 VANESSA THE CRESCENT 2 | 2027 | KINGSGROVE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396347 | REP OE S006480 CHRISTINA MILLER | 2027 | VILLAWOOD | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396348 | REP OE S001563 TOELLE ST. | 2027 | ROZELLE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396349 | REP OE S002046 KING PALMERSTON NO.1 | 2027 | HORNSBY | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396350 | REP OE S002200 CHAMPION PLUGS | 2027 | ALEXANDRIA | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396351 | REP OE S002185 NATIONAL SPRINGS NO.1 | 2028 | ALEXANDRIA | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396352 | REP OE S001282 EXELL ST | 2028 | BANKSMEADOW | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396353 | REP OE S002042 SHEFFIELD RHYL NO.1 | 2028 | AUBURN | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396354 | REP OE S001899 HARBOUR MOSMAN | 2028 | MOSMAN | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396356 | REP OE S002480 ROSEBERY EPSOM | 2028 | ROSEBERY | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396357 | REP OE S009493 DAVIES KENT | 2028 | TAREN POINT | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396360 | REP OE S002540 DAISY CAR NO1 | 2028 | REVESBY | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396361 | REP OE S002378 COURLAND ST | 2028 | FIVE DOCK | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396364 | REP OE S002703 SHORT FAIR NO1 | 2028 | BANKSTOWN | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396366 | REP OE S001338 ADDERLEY STATION | 2028 | AUBURN | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396367 | REP OE S002799 CATHERINE MOORE | 2028 | LEICHHARDT | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396368 | REP OE S002972 STATION PRINCE | 2028 | TEMPE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396369 | REP OE S000723 EDITH ST | 2028 | ST PETERS | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396370 | REP OE S000897 CHISHOLM PRINCES | 2028 | AUBURN | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396371 | REP OE S002939 ANEMBO BAMBIL | 2028 | BEROWRA | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396372 | REP OE S003110 CARTER HILL NO.1 | 2028 | LIDCOMBE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396373 | REP OE S003142 SHORT BALLAST | 2029 | BIRCHGROVE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396374 | REP OE S009622 BATH GARNETT | 2029 | KIRRAWEE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396375 | REP OE S009610 OCEAN GROVE AVE | 2029 | CRONULLA | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396376 | REP OE S003287 GEORGE CONWAY | 2029 | CONCORD WEST | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396377 | REP OE S009631 TASMAN ST WEST | 2029 | KURNELL | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396378 | REP OE S003324 GRACE BROS FLEM NO2 | 2029 | LIDCOMBE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396380 | REP OE S003787 CARNARVON SKARRATT | 2029 | SILVERWATER | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396381 | REP OE S003585 BONDS PATRICK | 2029 | ROSELANDS | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396382 | REP OE S003757 PHILLIP BOURKE | 2029 | WATERLOO | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396383 | REP OE S009608 MONRO AVE. | 2029 | KIRRAWEE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396385 | REP OE S009152 BAY NAMCO | 2029 | CARINGBAH | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396386 | REP OE S003537 MARIGOLD BYRNE | 2029 | REVESBY | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396387 | REP OE S004148 TARRO PAM | 2029 | REVESBY | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396388 | REP OE S004160 HIGHGATE ST | 2029 | AUBURN | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396390 | REP OE S004949 BRIDGE SHERBROOK | 2029 | HORNSBY | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396391 | REP OE S004229 MEMORIAL MONA VALE | 2030 | ST IVES | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396392 | REP OE S004842 LLOYD GEORGE AVE | 2030 | CONCORD | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396393 | REP OE S005022 FRIENDSHIP CHARLOTTE | 2030 | PORT BOTANY | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396394 | REP OE S004780 WAREEMBA HAMPDEN | 2030 | WAREEMBA | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396395 | REP OE S005441 RAWSON PARRAMATTA NO 2 | 2030 | AUBURN | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396396 | REP OE S012354 BMI QUARRY BUSHELLS NO3 | 2030 | PEATS RIDGE | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396399 | REP OE S005962 LOVE NB NO 3 | 2030 | STRATHFIELD SOUTH | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396400 | REP OE S005716 CONRAIL PARK MCPHERSON | 2030 | BANKSMEADOW | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396401 | REP OE S005911 SHADDOCK METAL POLISHER | 2030 | VILLAWOOD | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396402 | REP OE S005889 STATE MAIL RALPH ST | 2030 | ALEXANDRIA | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.42 | Outdoor Enclosure Substations | 1700396403 | REP OE S005916 BANK BOWMAN | 2030 | PYRMONT | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700176317 | REP SCB Sub - S001377 LITTLE SPRING BERR | 2027 | NORTH SYDNEY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700176320 | REP SCB Sub - S003352 LITTLE SPRING SPRI | 2027 | NORTH SYDNEY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700198878 | REP HVCB S001015 BROUGHTON GREENWAY | 2027 | KIRRIBILLI | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700176326 | REP SCB Sub - S001927 FULLERTON ST. | 2027 | WOOLLAHRA | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700176328 | REP SCB Sub - S003454 CHANDOS CHRISTIE | 2027 | ST LEONARDS | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222028 | REP SCB SUB S005885 ARCHER DAVID JONES | 2027 | CHATSWOOD | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222051 | REP SCB SUB S004567 DILLON ST | 2027 | DARLINGHURST | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222058 | REP SCB SUB S003299 MILLER INVESTMENTS | 2027 | NORTH SYDNEY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222061 | REP SCB S001856 MITCHELL POINT | 2027 | DARLING POINT | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222063 | REP SCB SUB S004000 NAPIER CHARLES | 2027 | NORTH SYDNEY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222065 | REP SCB SUB S003416 NICHOLSON OXLEY | 2027 | ST LEONARDS | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222075 | REP SCB S008072 RNS HOSPITAL NO 6 | 2027 | ST LEONARDS | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700222090 | REP SCB SUB S007271 WATERLOO MACQUARIE N | 2027 | MACQUARIE PARK | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235239 | REP HVCB_L S000689 Denistone Rd | 2027 | EASTWOOD | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235317 | REP HVCB_P4 S001397 Ralph Symonds | 2027 | WENTWORTH POINT | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235318 | REP HVCB_P4 S001530 Maritime Services No | 2027 | ROZELLE | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235363 | REP HVCB_J18 S002577 Stephen Swin | 2027 | BANKSMEADOW | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235365 | REP HVCB_P4 S000123 Johnson Queen | 2028 | ALEXANDRIA | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235414 | REP HVCB_L S000986 Egg Board | 2028 | LIDCOMBE | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235328 | REP HVCB_L S005325 Waterloo Macquarie No | 2028 | MACQUARIE PARK | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235374 | REP HVCB_L S005326 Waterloo Macquarie No | 2028 | MACQUARIE PARK | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235419 | REP HVCB_P4 S005931 Ici Friendship Rd | 2028 | PORT BOTANY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235420 | REP HVCB_L S005414 Tech College No 2 | 2028 | ULTIMO | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235437 | REP HVCB_F150 S001074 Unitec | 2028 | KENSINGTON | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235423 | REP HVCB_J18 S002420 Bankstown Square No | 2028 | BANKSTOWN | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235441 | REP HVCB_OLX S003239 Merewether Building | 2028 | DARLINGTON | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235404 | REP HVCB_P4 S016124 Ashburner Street | 2029 | MANLY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235405 | REP HVCB_P4 S005639 Khartoum Talavera No | 2029 | MACQUARIE PARK | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235407 | REP HVCB_L S001145 Amp North Sydney No.1 | 2029 | NORTH SYDNEY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235488 | REP HVCB_J18 S000386 Crewe Place | 2029 | ROSEBERY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235489 | REP HVCB_J18 S005514 Macarthur Systrum | 2029 | ULTIMO | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235493 | REP HVCB_F150 S006445 Darling Harbour Ma | 2029 | SYDNEY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235494 | REP HVCB_F150 S000067 Foveaux St | 2029 | SURRY HILLS | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235495 | REP HVCB_LMT S000774 Eastern Suburbs New | 2029 | ALEXANDRIA | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235523 | REP HVCB_F100 S000063 Little Riley St | 2030 | SURRY HILLS | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235536 | REP HVCB_F100 S000189 Hoddle St | 2030 | PADDINGTON | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235537 | REP HVCB_F100 S000530 Bon Accord Ave | 2030 | BONDI JUNCTION | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235540 | REP HVCB_F100 S000445 Hands Lane | 2030 | SURRY HILLS | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.43 | Circuit Breaker Replacement - HV | 1700235448 | REP HVCB_F100 S000546 Artarmon Road | 2030 | WILLOUGHBY | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk.
REP_01.02.61 | Intertripping Schemes - DC | 1700438688 | REP 11KV IT PROT S000123 JOHNSON QUEEN | 2027 | ALEXANDRIA | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438696 | REP 11KV IT PROT S002420 BANKSTOWN SQUAR | 2027 | BANKSTOWN | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438698 | REP 11KV IT PROT S002533 GOLDMAN LANE | 2027 | DOUBLE BAY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438701 | REP 11KV IT PROT S002582 ANZAC WAL | 2027 | KINGSFORD | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438702 | REP 11KV IT PROT S002797 FREDERICK HERBE | 2027 | ARTARMON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438704 | REP 11KV IT PROT S003002 ARTHUR MOUNT NO | 2027 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438705 | REP 11KV IT PROT S002975 CLIFF LAVENDER | 2027 | MILSONS POINT | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438706 | REP 11KV IT PROT S002959 KIPPAX HOLT NO | 2027 | SURRY HILLS | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438707 | REP 11KV IT PROT S003239 MEREWETHER BUIL | 2027 | DARLINGTON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438709 | REP 11KV IT PROT S003167 NEW MCLEAN ST | 2028 | EDGECLIFF | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438710 | REP 11KV IT PROT S003542 LOVE NB NO 1 | 2028 | STRATHFIELD SOUTH | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438713 | REP 11KV IT PROT S003718 HILL AGL CENTRE | 2028 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438714 | REP 11KV IT PROT S002960 KIPPAX HOLT NO. | 2028 | SURRY HILLS | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438715 | REP 11KV IT PROT S003666 MECH. ENGINEERI | 2028 | DARLINGTON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438717 | REP 11KV IT PROT S004091 LIVERPOOL NITH | 2028 | SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438718 | REP 11KV IT PROT S003915 MILLER NORTHPOI | 2028 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438719 | REP 11KV IT PROT S003762 GEORGE PORT | 2028 | WATERLOO | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438720 | REP 11KV IT PROT S004186 EASTWOOD SHOPPI | 2028 | EASTWOOD | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438722 | REP 11KV IT PROT S004590 CARROLL LANE | 2029 | BONDI JUNCTION | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438724 | REP 11KV IT PROT S005325 WATERLOO MACQUA | 2029 | MACQUARIE PARK | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2029 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438725 | REP 11KV IT PROT S005326 WATERLOO MACQUA | 2029 | MACQUARIE PARK | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2029 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438726 | REP 11KV IT PROT S005051 TELECOM NORTH S | 2029 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438728 | REP 11KV IT PROT S006235 LITTLE WALKER M | 2029 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2029 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438730 | REP 11KV IT PROT S006388 SPRING WESTFIEL | 2029 | CHATSWOOD | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2029 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438732 | REP 11KV IT PROT S006445 DARLING HARBOUR | 2029 | SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2029 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438733 | REP 11KV IT PROT S006494 RICKARD APPIAN | 2029 | BANKSTOWN | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2029 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438734 | REP 11KV IT PROT S006642 BRADFIELD PARK | 2029 | MILSONS POINT | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438735 | REP 11KV IT PROT S006643 NORTH PYLON | 2030 | MILSONS POINT | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438736 | REP 11KV IT PROT S007215 MUIR HUME | 2030 | CHULLORA | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438737 | REP 11KV IT PROT S000234 VICTORIA CHATSW | 2030 | CHATSWOOD | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438738 | REP 11KV IT PROT S000402 SYDNEY CASINO N | 2030 | PYRMONT | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438739 | REP 11KV IT PROT S000371 SYDNEY CASINO N | 2030 | PYRMONT | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438740 | REP 11KV IT PROT S000387 SYDNEY CASINO N | 2030 | PYRMONT | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438527 | REP SCADA SYSTEM TS07150 PYRMONT STS | 2027 | PYRMONT | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438534 | REP SCADA SYSTEM ZN04990 CITY CENTRAL | 2028 | SYDNEY | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700501072 | REP SCADA SYSTEM TS07140 BUNNERONG NORTH | 2028 | MATRAVILLE | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2028 | No Change
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700660569 | REP SCADA SYSTEM ZN09550 GWAWLEY BAY | 2029 | MIRANDA | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2029 | No Change
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438617 | REP SCADA SCHEME TW07280 CHULLORA STSS | 2029 | STRATHFIELD | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438536 | REP SCADA SYSTEM ZN07900 CAMPBELL ST | 2030 | SURRY HILLS | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700786128 | REP SCADA SYSTEM ZN01610 HOMEBUSH BAY | 2030 | HOMEBUSH BAY | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374868 | REP NER X3 TS07220 WILLOUGHBY | 2027 | ARTARMON | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374872 | REP NER X TS00406 MITCHELL LINE | 2027 | MUSWELLBROOK | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700759698 | REP NER Y TS00406 MITCHELL LINE | 2027 | MUSWELLBROOK | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374873 | REP NER X3 TS07140 BUNNERONG NORTH | 2027 | MATRAVILLE | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700757011 | REP NER Y3 TS07140 BUNNERONG NORTH | 2027 | MATRAVILLE | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700757012 | REP NER Z3 TS07140 BUNNERONG NORTH | 2028 | MATRAVILLE | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374874 | REP NER X3 TS00409 SINGLETON | 2028 | MAISON DIEU | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700757021 | REP NER Y3 TS00409 SINGLETON | 2028 | MAISON DIEU | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374865 | REP NER R1 TS07170 SURRY HILLS | 2028 | SURRY HILLS | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700757025 | REP NER R2 TS07170 SURRY HILLS | 2028 | SURRY HILLS | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700757026 | REP NER R3 TS07170 SURRY HILLS | 2029 | SURRY HILLS | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374871 | REP NER X3 TS07150 PYRMONT | 2029 | PYRMONT | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700757017 | REP NER Y3 TS07150 PYRMONT | 2029 | PYRMONT | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700214276 | REP 226m CONSAC HS24852 SOUTH SEAS DRIVE | 2027 | ASHTONFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700214317 | REP 393m CONSAC HS54095_24922 GREENHILLS | 2027 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700214251 | REP 170m CONSAC HP46037_46037 ABERGLASSL | 2027 | RUTHERFORD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700214255 | REP 369m CONSAC HP52319_52319 OMARU | 2027 | CESSNOCK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700214250 | REP 184m CONSAC HP01685_1685 MAITLAND RD | 2027 | BOLWARRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700189434 | REP 573M CONSAC S004245_3 UPPER AVENUE R | 2027 | MOSMAN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700189439 | REP 133M CONSAC S010181_2 OCEAN ST STH | 2027 | PENSHURST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700194094 | S.17085 dist #2 - white powder | 2027 | WHEELER HEIGHTS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700197217 | REP 245m CONSAC S000380_2 BADHAM AVE E N | 2027 | MOSMAN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700197218 | REP 309m CONSAC S000380_3 BADHAM AVE CEN | 2027 | MOSMAN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700197219 | REP 560m CONSAC S000380_4 BADHAM AVE W N | 2027 | MOSMAN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700251499 | REP 130M HDPE S016980_3 SYDNEY RD W UG & | 2027 | BALGOWLAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700287694 | REP 119m CONSAC S048911_3 WAVERLEY COUNC | 2027 | BONDI JUNCTION | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700287696 | REP 370m CONSAC S036083_4 WALLAROY RD | 2027 | WOOLLAHRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700287697 | REP 311m CONSAC S035856_1 MANNING PINE | 2027 | DOUBLE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700287716 | REP 150m CONSAC S002396_3 ASHFIELD CIVIC | 2027 | ASHFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700287721 | REP 223m CONSAC S035856_2 MANNING PINE | 2027 | DOUBLE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700287736 | REP 125m CONSAC S004134_2 MILPERRA FITZ | 2027 | REVESBY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700287737 | REP 156m CONSAC S007342_2 WALDRON CAMPBE | 2027 | CHESTER HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700287740 | REP 147m CONSAC S047442_1 CHERRY PACIFIC | 2027 | WARRAWEE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700287744 | REP 181m CONSAC S004471_1 FONTENOY LAND | 2027 | MACQUARIE PARK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700501814 | REP 190m CONSAC HS38367_24216 METFORD No | 2027 | METFORD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1700501849 | REP 261m CONSAC PT10329_1 HILLVIEW PROME | 2027 | SANS SOUCI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | Underground Cable Replacement - LV (km) | 1201074932 | White powder on Dist.2 cable at S16214 | 2027 | MONA VALE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.12 | LV Metallic Sheathed Cables | 1700785982 | REP 340M MET SHEATH LV CABLE S1013 Dist6 | 2029 | SYDNEY | Ausgrid has approximately 785km of Low Voltage underground metallic sheathed cable which supply electricity from distribution substations to customers. LV metallic sheathed cable failures can result in consequences including safety risks, fire risk, unserved energy and other risks. A planned replacement strategy has been adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment.
REP_04.02.12 | LV Metallic Sheathed Cables | 1700785994 | REP 310m MET SHEATH LV CABLE S1779 Dist8 | 2029 | SYDNEY | Ausgrid has approximately 785km of Low Voltage underground metallic sheathed cable which supply electricity from distribution substations to customers. LV metallic sheathed cable failures can result in consequences including safety risks, fire risk, unserved energy and other risks. A planned replacement strategy has been adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment.
REP_04.04.01 | Overhead Mains Replacement - LV (km) | 1201727165 | LowLV 4.06mFootpath 2019 defectNAR154688 | 2030 | GYMEA BAY | Degradation of overhead conductors and conductor ties can result in fallen conductors which pose risks to public safety and loss of network supply. This program funds the replacement of conditionally failed LV overhead conductor. It is to replace the overhead conductor including the replacements of all conductor phases in any conductor bay or strain section. The scope also includes sections of dedicated LV circuits of bare or PVC insulated construction that must be replaced when dthey are not able to be removed through transferral to LV mains.
REP_04.04.01 | Overhead Mains Replacement - LV (km) | 1700326363 | REP 120M LVOH LE21508_LE21511 COMER ST | 2030 | BURWOOD | Degradation of overhead conductors and conductor ties can result in fallen conductors which pose risks to public safety and loss of network supply. This program funds the replacement of conditionally failed LV overhead conductor. It is to replace the overhead conductor including the replacements of all conductor phases in any conductor bay or strain section. The scope also includes sections of dedicated LV circuits of bare or PVC insulated construction that must be replaced when dthey are not able to be removed through transferral to LV mains.
REP_04.04.01 | Overhead Mains Replacement - LV (km) | 1202233081 | REP LVOH S4646_1 PY00261 | 2030 | WEST PYMBLE | Degradation of overhead conductors and conductor ties can result in fallen conductors which pose risks to public safety and loss of network supply. This program funds the replacement of conditionally failed LV overhead conductor. It is to replace the overhead conductor including the replacements of all conductor phases in any conductor bay or strain section. The scope also includes sections of dedicated LV circuits of bare or PVC insulated construction that must be replaced when dthey are not able to be removed through transferral to LV mains.
REP_04.04.02 | Underground Cable Replacement - HV (km) | 1700642148 | REP 250M HVUG ZN1290 P8 | 2030 | VILLAWOOD | 11kv and 5kV underground cables experience failures primarily due to age related degradation, moisture ingress or mechanical damage. The risks of failures may include network fires, public safety and loss of supply. This program funds the replacement of conditionally failure HV underground cables and the replacement of structurally/conditionally failure sections of the pit and duct system within the Sydney CBD. The scope is 'like for like' replacement.
REP_04.04.02 | Underground Cable Replacement - HV (km) | 1700642149 | REP 250M HVUG ZN1290 P11 | 2030 | VILLAWOOD | 11kv and 5kV underground cables experience failures primarily due to age related degradation, moisture ingress or mechanical damage. The risks of failures may include network fires, public safety and loss of supply. This program funds the replacement of conditionally failure HV underground cables and the replacement of structurally/conditionally failure sections of the pit and duct system within the Sydney CBD. The scope is 'like for like' replacement.
REP_04.04.02 | Underground Cable Replacement - HV (km) | 1700642150 | REP 250M HVUG ZN1290 P12 | 2030 | VILLAWOOD | 11kv and 5kV underground cables experience failures primarily due to age related degradation, moisture ingress or mechanical damage. The risks of failures may include network fires, public safety and loss of supply. This program funds the replacement of conditionally failure HV underground cables and the replacement of structurally/conditionally failure sections of the pit and duct system within the Sydney CBD. The scope is 'like for like' replacement.
REP_04.04.02 | Underground Cable Replacement - HV (km) | 1700643644 | REP 250M HVUG ZN1290 P2 | 2030 | VILLAWOOD | 11kv and 5kV underground cables experience failures primarily due to age related degradation, moisture ingress or mechanical damage. The risks of failures may include network fires, public safety and loss of supply. This program funds the replacement of conditionally failure HV underground cables and the replacement of structurally/conditionally failure sections of the pit and duct system within the Sydney CBD. The scope is 'like for like' replacement.
REP_05.02.01-5 | Tower Replacement | 1700681449 | TRANSMISSION FEEDER & TOWER RECOVERY | 2027 | Homebush | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700795506 | REP TOWER FF00511 9M1-9M2-043 | 2027 | FRENCHS FOREST | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700379143 | REP TOWER 952-001 FDR 95A | 2027 | KILLINGWORTH | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700440038 | REP TWR REPLACEMENT PRIORITY DESIGN | 2027 | Homebush | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | No Change
REP_05.02.01-5 | Tower Replacement | 1700550482 | REP COMMS TOWER STRUCTURAL Black mntn | 2027 | WINGEN | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642438 | REP TOWER KL488 FDR 916/917 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642435 | REP TOWER KL487 FDR 916/917 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642422 | REP TOWER KL486 FDR 916/917 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642416 | REP TOWER KL485 FDR 916/917 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2028 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642436 | REP TOWER KL484 FDR 916/917 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2028 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642425 | REP TOWER KL489 FDR 916/917 | 2029 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642433 | REP TOWER CR9147 FDR 916/917 | 2029 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642440 | REP TOWER CR9148 FDR 916/917 | 2029 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642443 | REP TOWER CR9145 FDR 916/917 | 2029 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2029 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642442 | REP TOWER CR9144 FDR 916/917 | 2029 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2029 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642444 | REP TOWER CR9143 FDR 916/917 | 2030 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2029 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642446 | REP TOWER CR9142 FDR 916/917 | 2030 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2029 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642445 | REP TOWER CR9141 FDR 916/917 | 2030 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2029 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642447 | REP TOWER CR9140 FDR 916/917 | 2030 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option.
REP_05.02.01-5 | Tower Replacement | 1700642448 | REP TOWER CR9139 FDR 916/917 | 2030 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option.
REP_05.02.29 | Replace ST Feeder OH Earth Wire | 1700311693 | REP OHEW 18km FDR 952 | 2028 | Newcastle | The overhead earth wire foroverhead feeders operating at 33kV, 66kV and 132kV have many different configurations and many different operating environments. Degradation of OHEWs can be influenced by their age, their design/markterial, their operating environment, the span length/conductor loading and other factors. The risk of OHEW failure is managed through established maintenance processes and their replacement when they have been conditionally failed. This program funds 'like for like' replacement of the conditionally failed portions of OHEW and equipment directly associated with the OHEW.
REP_05.02.29 | Replace ST Feeder OH Earth Wire | 1700311695 | REP OHEW 20km FDR 96B | 2029 | Newcastle | The overhead earth wire foroverhead feeders operating at 33kV, 66kV and 132kV have many different configurations and many different operating environments. Degradation of OHEWs can be influenced by their age, their design/markterial, their operating environment, the span length/conductor loading and other factors. The risk of OHEW failure is managed through established maintenance processes and their replacement when they have been conditionally failed. This program funds 'like for like' replacement of the conditionally failed portions of OHEW and equipment directly associated with the OHEW.
REP_05.02.29 | Replace ST Feeder OH Earth Wire | 1700395445 | REP 3500m OHEW_TWR13C_C/BURY STS FD910 | 2029 | BELFIELD | The overhead earth wire foroverhead feeders operating at 33kV, 66kV and 132kV have many different configurations and many different operating environments. Degradation of OHEWs can be influenced by their age, their design/markterial, their operating environment, the span length/conductor loading and other factors. The risk of OHEW failure is managed through established maintenance processes and their replacement when they have been conditionally failed. This program funds 'like for like' replacement of the conditionally failed portions of OHEW and equipment directly associated with the OHEW.
REP_05.02.29 | Replace ST Feeder OH Earth Wire | 1700395446 | REP 4500m OHEW_TWR13C_C/BURY STS FD911 | 2029 | BELFIELD | The overhead earth wire foroverhead feeders operating at 33kV, 66kV and 132kV have many different configurations and many different operating environments. Degradation of OHEWs can be influenced by their age, their design/markterial, their operating environment, the span length/conductor loading and other factors. The risk of OHEW failure is managed through established maintenance processes and their replacement when they have been conditionally failed. This program funds 'like for like' replacement of the conditionally failed portions of OHEW and equipment directly associated with the OHEW.
REP_05.02.29 | Replace ST Feeder OH Earth Wire | 1700395447 | REP 2700m OHEW_TWR3C_CHULLORA SS FD910 | 2029 | STRATHFIELD SOUTH | The overhead earth wire foroverhead feeders operating at 33kV, 66kV and 132kV have many different configurations and many different operating environments. Degradation of OHEWs can be influenced by their age, their design/markterial, their operating environment, the span length/conductor loading and other factors. The risk of OHEW failure is managed through established maintenance processes and their replacement when they have been conditionally failed. This program funds 'like for like' replacement of the conditionally failed portions of OHEW and equipment directly associated with the OHEW.
REP_05.02.29 | Replace ST Feeder OH Earth Wire | 1700395449 | REP 3000m OHEW_TWR3C_CHULLORA SS FD911 | 2029 | STRATHFIELD SOUTH | The overhead earth wire foroverhead feeders operating at 33kV, 66kV and 132kV have many different configurations and many different operating environments. Degradation of OHEWs can be influenced by their age, their design/markterial, their operating environment, the span length/conductor loading and other factors. The risk of OHEW failure is managed through established maintenance processes and their replacement when they have been conditionally failed. This program funds 'like for like' replacement of the conditionally failed portions of OHEW and equipment directly associated with the OHEW.