## STEPS
STEP 1 | Define 'incident'
STEP 2 | Determine frequency of incident (F)
STEP 3 | Define 'impact'
STEP 4 | Determine magnitude of impact, l, dB, etc. - could be distributed
STEP 5 | Define shape/size of footprint, m2, people, volume etc (E) - could be distributed
STEP 6 | Determine weighted average sensitivity of footprint (S) - using sensitivity table
STEP 7 | Determine RISK (FxExS)
Rainfall
| Standard rainfall event = | 10mm
| Big rainfall event = | 30mm
Hugh rainfall event =
| Annual rainfall = | 1200mm
Transmisison cable trenches
| Oil migration groundwater - sand (2,000L) = | 40m radius
| Oil migration along trench - other (2,000L) = | 200m
Oil on dirt
1000L = (10m)2 or 100 sqm
Oil on hard surface
10L = (10m)2 or 100sqm
Oil on water
10L = (10m)2 or 100sqm
| Offensive noise = | 40dB ~40m from zn transformer
Incident frequency - F
Impact 1
Impact 2
Impact ...
Magnitude of pollutant 1
Size of footprint 1- E
Sensitivity of footprint 1- S
RISK 1
= FxExS
REFERENCE TABLE
Litres, dB etc.
2. Area, number of people etc.
1. Shape of footprint.
Incident
Bunds, slope, soil type, drainage, walls etc.
REFERENCE TABLE
Failure rates, number of equip etc.

## Sensitivity Reference Table
Environmental Sensitivity Reference Table
Risk Units | Failure to comply with a legislative requirement | Intense flow of contaminated, hazardous or dangerous substances (eg PCB contaminted oil, pesticides etc.) | Intense flow of un contaminated oil | Intense flow of water - contaminated with traces of oil <10ppm | Intense flow of water - contaminated with sediment | Cable oil, transformer oil contaminated land etc. | Operatoinal noise - Zone transformer (exceed guidelines) | Construction noise & Vibration (exceeding guidelines) | Disrupting transport (construction) | EMF health concerns (4mG issue) - existing infrastructure | EMF health concerns (4mG issue) - proposed infrastructure
| Per incident* | Per/1000L | Per/1000L | Per/1000L | Per/1000L | Per/1000L | Per/10 receivers | Per/10 receivers | Per significant blockage | Per/year | Per/year
10000 | Impact is likely to cause a significant adverse and irreversible reaction with which the environment cannot cope. The public is likely to be outraged. | Drinking water catchment, accessible bore water, Ramsar Wetland, threatened species, critical habitat, SEPP 14 - Coastal Wetlands, SEPP 26 - Littoral Rainforests, Natural waterbody, urban bushland.
1000 | Somewhere in between | National Park, urban bushland, Residential area, socially sensitive area, urban drainage, CBD | Drinking water catchment, accessible bore water, Ramsar Wetland, threatened species, critical habitat, SEPP 14 - Coastal Wetlands, SEPP 26 - Littoral Rainforests, Natural waterbody, urban bushland. |  |  | Drinking water catchment, accessible bore water, Ramsar Wetland, Natural waterbody.
100 | Impact is likely to cause an adverse reaction with which the environment cannot easily cope. The general public will be interested. | Commercial | National Park, urban bushland, Residential area, socially sensitive area, urban drainage, CBD | Drinking water catchment, accessible bore water, Ramsar Wetland, threatened species, critical habitat, SEPP 14 - Coastal Wetlands, SEPP 26 - Littoral Rainforests, Natural waterbody, urban bushland. | Drinking water catchment, accessible bore water, Ramsar Wetland, threatened species, critical habitat, SEPP 14 - Coastal Wetlands, SEPP 26 - Littoral Rainforests, Natural waterbody, urban bushland. | Contained within the ground | Childcare centre, school, residential area, socially sensitive area etc. |  |  | Schools, childcare centres, places where children congrate etc.
10 | Somewhere in between | Industrial area, contained within ground | Commercial | National Park, urban bushland, Residential area, socially sensitive area, urban drainage, CBD | National Park, urban bushland, Residential area, socially sensitive area, urban drainage, CBD |  | Commercial area (restaurants, shops etc.) |  | Freeways, Highways, railways etc. | Residential areas | Schools, childcare centres, places where children congrate etc.
1 | Impact is likely to cause an adverse reaction, however, it can be readily reversed or may be accepted. |  | Industrial area, contained within ground | Commercial | Commercial |  |  | Childcare centre, school, residential area, socially sensitive area etc. | Major link roads | Office areas, commercial areas etc. | Residential areas
0.1 | Somewhere in between | Contained within bunded area |  | Industrial area, contained within ground | Industrial area, contained within ground |  | Rural area, industrial area | Commercial area (restaurants, shops etc.) |  |  | Office areas, commercial areas etc.
0.01 | Impact may cause a reaction, however, the environment can readily handle the impact and the public will not be interested. |  | Contained within bunded area

## RISK ASSESSMENT
EGN 420: RELATIVE RISK MODEL - OIL FILLED EQUIPMENT
Version 14 - 9 May 2014
STEP 1 - Enter substation/transformer details
Oil Filled Equipment
| Volume of oil stored | 400 | L
STEP 2 - Enter details of flow path to nearest downstream waterway
| Discharge Path | Area 1 | Area 2 | Area 3 | Area 4 | Area 5 | Area 6
| Length of area (downstream) (m) | 5 | 15 | 3 | 0 | 0 | 0
Slope
| Additional storage capacity | 0 | 0 | 0 | 0 | 0 | 0
Flow path surface type
Sensitivity of flow path
Sensitivity of waterway
| Oil leaving Substation | 20
| Oil entering area A | 20 | 0 | 0 | 0 | 0 | 0 | 0
| Holding capacity of area | 125 | 150 | 150 | 0 | 0 | 0
| Oil left in area | 20 | 0 | 0 | 0 | 0 | 0
| Oil leaving area | 0 | 0 | 0 | 0 | 0 | 0
| Sensitivity score | 500 | 500 | 5 | 500 | 500 | 500
| Risk due to oil in waterway | 0
| RISK | 10000 | 0 | 0 | 0 | 0 | 0
| RISK TOTAL | 10000
18
INSTRUCTIONS
1. Use this calculator to determine the risk to the nearest waterway of installing oil filled equipment at a certain location. If you have multiple location options you can complete the calculator for each option and rank the options accordingly. The option with the lowest risk is the preferred option.
2. Complete Step 1 by indicating the type of oil filled equipment you will be installing and the volume of oil to be stored in it.
3. Evaluate the location of the oil filled equipment you will be installing, locate the nearest waterway. Determine how many different types of areas are along the flow path between the location and the nearest waterway. There may only be one type of area along the flow path or there may be many. This calculator only allows for six different types of areas.
4. Complete Step 2 by filling in the criteria for each of the different areas along the flow path. Indicate the sensitivity of the nearest waterway. Refer to the 'RISK TOTAL'. This is the risk for installing the oil filled equipment at the calculated location.
Note on B18: Measured horizontally (eg a vertical cliff would have a length of 0) Stop once you have reached a waterway

## DATA TABLES
| Substation type | Holding capacity |  |  | 1 | 95% | 0%
1 | Chamber | 95%
2 | H Type Kiosk | 50%
3 | J Type Kiosk | 90%
4 | K Type Kiosk | 90%
5 | L Type Kiosk | 90%
6 | Pole Top | 0%
[6 empty] | Area 1 | Area 2 | Area 3 | Area 4 | Area 5 | Area 6
| Slope |  |  |  | Slope ID | 2 | 2 | 2 | 1 | 1 | 1
|  | <5% | Flat
|  | >5% | Steep
|  | Capacity (L) per 10m |  |  |  | ID Surface type
| Surface | <5% | >5% |  |  | 5 | 4 | 8 | 1 | 1 | 1
| Concrete | 30 | 15
| Asphalt | 40 | 20
| Bricks / Pavers | 100 | 50
| Stormwater pit and pipe system | 200 | 100
| Bare Earth | 500 | 250
| Grass | 670 | 335
| Sand | 1000 | 500
| Long grass/reeds | 1000 | 500
|  | Relative Risk |  |  |  | ID Sensitivity of area
| Sensitivity | <2ppm PCB |  |  |  | 1 | 1 | 4 | 1 | 1 | 1
| Gutter/stormwater drain | 500
| Residential property recreational park | 10
| Commercial/Industrial property | 5
| Public footpath | 5
| Depot / substation | 1
| Sensitivity of waterway |  | 1 | 10000
1 | Protected wetlands | 10000
2 | Waterway | 1000
3 | Tidal canal | 800
| Substation type | Oil Volume (litres)
| CITY & SUBURBAN CHAMBER TX - 750 kVA | 1200
| CITY & SUBURBAN CHAMBER TX - 1000 kVA | 1050
| CITY & SUBURBAN CHAMBER TX - 1500 kVA | 1480
| J TYPE KIOSK TX - 315 kVA | 520
| J TYPE KIOSK TX - 400 kVA | 510
| L TYPE KIOSK TX - 400 kVA | 544
| L TYPE KIOSK TX - 600 kVA | 623
| L TYPE KIOSK TX - 800 kVA | 821
| L TYPE KIOSK TX - 1000 kVA | 787
| K TYPE KIOSK TX - 1500 kVA | 1450
| POLE TOP TX (3ph) - 25 kVA | 90
| POLE TOP TX (3ph) - 63 kVA | 204
| POLE TOP TX (3ph) - 100 kVA | 290
| POLE TOP TX (3ph) - 200 kVA | 320
| POLE TOP TX (3ph) - 400 kVA | 480
| POLE TOP TX (1ph) - 16 kVA | 50
| POLE TOP TX (1ph) - 25 kVA | 59
| POLE TOP TX (1ph) - 25 (22kV) | 80
| POLE TOP TX (1ph) - 25 SWER | 60
| POLE TOP TX (1ph) - 63 | 160
| E TYPE KIOSK REPLACEMENT TX - 600 kVA | 590
| E TYPE KIOSK REPLACEMENT TX - 600 (dual voltage) kVA | 610
| E TYPE KIOSK REPLACEMENT TX - 750 kVA | 980
| E TYPE KIOSK REPLACEMENT TX - 1000 kVA | 950
| CBD VAULT TX - 400 kVA | 705
| CBD VAULT TX - 750 kVA | 1000
| CBD VAULT TX - 1000 kVA | 1055
Note on G10: Flowing water should have a slope >5%